SIX MONTH SURVEILLANCE

HOMOGENEOUS ACBM RECORDS	Date of Inspection: __09/28/09_________

District: Chico Unified School District	Inspector: Dale Hayes

School: Chapman Elementary School	Building: Unit A (FKA G)

| Material Class | Material | Homo. Mat. # | % Asb. | Ft2/L.F. | Location | Condition: Code & Comments | Friable Yes/No |
| --- | --- | --- | --- | --- | --- | --- | --- |
| T | MUD JOINT | 1 | 1-5% | UNDETERMINED | THROUGHOUT | (11) SAMPLE HMS-CPM-03 COLLECTED ON 4/9/88. | Y |
| M | TRANSITE PANELS | 2 | ASSUMED | UNDETERMINED | THROUGHOUT | (1) (2) By door room 21 | N |
| M | 12" VFT CREAM | 3 | None Detectedb | 400 S | CLASSROOMS 1, 2, 6, & 7 | (13) CUSD sample taken 12/26/07 chp01-chp 04 | N |

School: Chapman Elementary School	Building: Unit D (FKA F)

| Material Class | Material | Homo. Mat. # | % Asb. | Ft2/L.F. | Location | Condition: Code & Comments | Friable Yes/No |
| --- | --- | --- | --- | --- | --- | --- | --- |
| M | 9" VFT | 4 | 1-5% | UNDETERMINED | THROUGHOUT EXCEPT IN LIBRARY | (1) (4) | N/A |
| M | 9" VFT | 5 | 1-5% | UNDETERMINED | THROUGHOUT EXCEPT IN LIBRARY | (1) (4) | N/A |
| M | TRANSITE PANELS | 6 | ASSUMED | 400 S | EXTERIOR | (1) (4) | N |

CONDITION CODE

General Condition:	(1) Good	(2)  Damaged	(3)  Significantly Damaged (25% or more)

Change in Condition:	(4) No		(5)  Yes (If Yes, explain under comments)

Abated:		(6) Repaired	(7)  Removed	(8)  Encapsulated	(9)  Enclosed   	(10) Isolated & Restricted

Miscellaneous:		(11) Inaccessible, no inspection data	    (12) Other (Explain under comments)   	 (13) Non-Asbestos/Not Inspected

CONSULT ORIGINAL AND SUPPLEMENTARY INSPECTION REPORTS FOR MATERIALS WITH TRACE AMOUNTS OF ASBESTOS

SIX MONTH SURVEILLANCE

HOMOGENEOUS ACBM RECORDS	Date of Inspection: __09/28/09_________

District: Chico Unified School District	Inspector: Dale Hayes

School: Chapman Elementary School	Building: Unit E (FKA C)

| Material Class | Material | Homo. Mat. # | % Asb. | Ft2/L.F. | Location | Condition: Code & Comments | Friable Yes/No |
| --- | --- | --- | --- | --- | --- | --- | --- |
| M | TRANSITE PANELS | 7 | ASSUMED | 400 S | EXTERIOR | (1) (4) | N |
| M | 12" VFT CREAM | 8 | None Detected | 3,600 S | CLASSROOMS 15-18 | (13) CUSD sample 12/26/07 chp 01-04 MODERNIZATION 1989 | N |

School: Chapman Elementary School	Building: Unit F (FKA A)

| Material Class | Material | Homo. Mat. # | % Asb. | Ft2/L.F. | Location | Condition: Code & Comments | Friable Yes/No |
| --- | --- | --- | --- | --- | --- | --- | --- |
| M | 9" VFT BROWN | 9 | 10-15% | UNDETERMINED | KITCHEN | (1) (2) 21 TILES MISSING | N |
| M | 12" VFT CREAM | 10 | None Detected | 3,600 S | MPR, CORRIDOR, AND OFFICES | (13) CUSD sample on 12/26/07 chp 01-04 MODERNIZATION 1989 | N |
| M | 12" ACT | 11 | NON ASBESTOS | 3,600 S | MPR, CORRIDOR, AND OFFICES | (13) CUSD SAMPLE COLLECTED ON 7/8/08 | N |
| S | PLASTER | 12 | NONE DETECTED | UNDETERMINED | KITCHEN | - CUSD SAMPLE Chp01COLLECTED 2/22/06 | N/A |

CONDITION CODE

General Condition:	(1) Good	(2)  Damaged	(3)  Significantly Damaged (25% or more)

Change in Condition:	(4) No		(5)  Yes (If Yes, explain under comments)

Abated:		(6) Repaired	(7)  Removed	(8)  Encapsulated	(9)  Enclosed   	(10) Isolated & Restricted

Miscellaneous:		(11) Inaccessible, no inspection data	    (12) Other (Explain under comments)   	 (13) Non-Asbestos/Not Inspected

CONSULT ORIGINAL AND SUPPLEMENTARY INSPECTION REPORTS FOR MATERIALS WITH TRACE AMOUNTS OF ASBESTOS

SIX MONTH SURVEILLANCE

HOMOGENEOUS ACBM RECORDS	Date of Inspection: __09/28/09_________

District: Chico Unified School District	Inspector: Dale Hayes

School: Chapman Elementary School	Building: Unit H (FKA B)

| Material Class | Material | Homo. Mat. # | % Asb. | Ft2/L.F. | Location | Condition: Code & Comments | Friable Yes/No |
| --- | --- | --- | --- | --- | --- | --- | --- |
| M | TRANSITE PANELS | 13 | ASSUMED | 400 S | EXTERIOR | (1) (4) | N |
| M | 12" VFT cream | 14 | None Detected | 3,600 S | CLASSROOMS 19-22 | (13) CUSD sample on 12/26/07 chp 01- chp 04 MODERNIZATION 1989 | N |

CONDITION CODE

General Condition:	(1) Good	(2)  Damaged	(3)  Significantly Damaged (25% or more)

Change in Condition:	(4) No		(5)  Yes (If Yes, explain under comments)

Abated:		(6) Repaired	(7)  Removed	(8)  Encapsulated	(9)  Enclosed   	(10) Isolated & Restricted

Miscellaneous:		(11) Inaccessible, no inspection data	    (12) Other (Explain under comments)   	 (13) Non-Asbestos/Not Inspected

CONSULT ORIGINAL AND SUPPLEMENTARY INSPECTION REPORTS FOR MATERIALS WITH TRACE AMOUNTS OF ASBESTOS