SIX MONTH SURVEILLANCE

HOMOGENEOUS ACBM RECORDS	Date of Inspection: __09/28/09______

District: Chico Unified School District	Inspector: Dale Hayes

School: Neal Dow Elementary School	Building: A

| Material Class | Material | Homo. Mat. # | % Asb. | Ft2/L.F. | Location | Condition: Code & Comments | Friable Yes/No |
| --- | --- | --- | --- | --- | --- | --- | --- |
| M | 12" ACT | 7 | NONE DETECTED | 18,500 S | THROUGHOUT ENTIRE BUILDING | (13) SAMPLE HMS-DOW-07 COLLECTED IN 1988. | N/A |
| M | 9" VFT CREAM | 8 | 3-7% CHRYSOTILE | 19,500 S | ADMINISTRATION AREA (900), ALL CLASSROOMS, AND HALLWAY, mpr | (1) (4) CUSD SAMPLE COLLECTED 7/30/07 | N |
| M | LINOLEUM TAN | 10 | 5-10% | 36 S | NURSE’S OFFICE RESTROOM (903) | (1) (4) | N |
| T | TSI | 11 | 25-30% | 2 L | ADMINISTRATION (900) ATTIC | (1) (10) SAMPLE HMS-DOW-11 COLLECTED ON 3/29/88. | Y |
| T | PIPE WRAP CORNER | 12 | 25-30% | 4 JOINTS | ADMINISTRATION ATTIC HALLWAY | (1) (10) SAMPLE HMS-DOW-12 COLLECTED ON 3/29/88. | Y |
| T | PIPE WRAP STRAIGHT | 13 | 35-40% | 310 L | ADMINISTRATION ATTIC HALLWAY | (1) (10) SAMPLE HMS-DOW-13 COLLECTED ON 3/29/88. | Y |
| T | LARGE PIPE WRAP STRAIGHT | 14 | 35-40% | 105 L | BOILER ROOM (913) | (1) (4) USED AS A STOREROOM. SAMPLE HMS-DOW-14 COLLECTED ON 3/29/88. | Y |

CONDITION CODE

General Condition:	(1) Good	(2)  Damaged	(3)  Significantly Damaged (25% or more)

Change in Condition:	(4) No		(5)  Yes (If Yes, explain under comments)

Abated:		(6) Repaired	(7)  Removed	(8)  Encapsulated	(9)  Enclosed   	(10) Isolated & Restricted

Miscellaneous:		(11) Inaccessible, no inspection data	    (12) Other (Explain under comments)   	 (13) Non-Asbestos/Not Inspected

CONSULT ORIGINAL AND SUPPLEMENTARY INSPECTION REPORTS FOR MATERIALS WITH TRACE AMOUNTS OF ASBESTOS

/tmp/in/input.doc

SIX MONTH SURVEILLANCE

HOMOGENEOUS ACBM RECORDS	Date of Inspection: __09/28/09______

District: Chico Unified School District	Inspector: Dale Hayes

School: Neal Dow Elementary School	Building: A

(Continued)

| Material Class | Material | Homo. Mat. # | % Asb. | Ft2/L.F. | Location | Condition: Code & Comments | Friable Yes/No |
| --- | --- | --- | --- | --- | --- | --- | --- |
| T | SMALL PIPE WRAP STRAIGHT | 15 | 30-35% | 70 L | BOILER ROOM (913) | (1) (4) SAMPLE HMS-DOW-15 COLLECTED ON 3/29/88. | Y |
| T | BREECHING | 16 | 20-30% | 65 L | BOILER ROOM (913) | (10) INSIDE BOILER UNIT. SAMPLE HMS-DOW-16 COLLECTED ON 3/29/88. | Y |
| S | PLASTER | 17 | TRACE | 540 S | RESTROOMS CEILING (905 & 905A) | (1) (4) SAMPLES HMS-DOW-17A-C COLLECTED ON 3/29/88. | N |
| M | DRYWALL & JOINT COMPOUND | 97 | ASSUMED | 2,800 S | OFFICE (900), STAFF ROOM (910), GIRL’S (906) & BOY’S (909) RESTROOMS, AND BOILER ROOM (913) | (1) (4) (5) GIRLS RESTROOM 906 NEEDS REPAIR | N |
| M | FIRE DOOR | 98 | ASSUMED | 2 DOORS | BOILER ROOMS (913) | (1) (4) | N |
| M | TRANSITE PANELS | 99 | ASSUMED | 5,000 F | ABOVE WINDOWS | (1) (4) | N |

CONDITION CODE

General Condition:	(1) Good	(2)  Damaged	(3)  Significantly Damaged (25% or more)

Change in Condition:	(4) No		(5)  Yes (If Yes, explain under comments)

Abated:		(6) Repaired	(7)  Removed	(8)  Encapsulated	(9)  Enclosed   	(10) Isolated & Restricted

Miscellaneous:		(11) Inaccessible, no inspection data	    (12) Other (Explain under comments)   	 (13) Non-Asbestos/Not Inspected

CONSULT ORIGINAL AND SUPPLEMENTARY INSPECTION REPORTS FOR MATERIALS WITH TRACE AMOUNTS OF ASBESTOS											/tmp/in/input.doc

SIX MONTH SURVEILLANCE

HOMOGENEOUS ACBM RECORDS	Date of Inspection: __09/28/09______

District: Chico Unified School District	Inspector: Dale Hayes

School: Neal Dow Elementary School	Building: C (FKA B)

| Material Class | Material | Homo. Mat. # | % Asb. | Ft2/L.F. | Location | Condition: Code & Comments | Friable Yes/No |
| --- | --- | --- | --- | --- | --- | --- | --- |
| S | PLASTER | 5 | 1-5% | 260 S | ROUND HOUSE QUAD CENTER CEILING | (2) PEELING PAINT GIRLS RESTROOM CEILING | N |
| M | 9" VFT TAN | 96 | ASSUMED | 150 S | ENTRY OF LIBRARY (923) & STORAGE ROOM (926) | (1) (4) ENTRY OF LIBRARY. (11) 9" VFT COULD BE UNDER THE CARPET. | N |
| M | TRANSITE PANELS | 99 | ASSUMED | 5,000 F | ABOVE WINDOWS – FRONT DOORS ONLY | (1) (4) | N |
| M | 2' X 4' FCP | 100 | ASSUMED | 5,000 S | ROUND HOUSE QUAD | (1) | N |
| M | DRYWALL | 101 | ASSUMED | UNDETERMINED | THROUGHOUT | (1) | N |

CONDITION CODE

General Condition:	(1) Good	(2)  Damaged	(3)  Significantly Damaged (25% or more)

Change in Condition:	(4) No		(5)  Yes (If Yes, explain under comments)

Abated:		(6) Repaired	(7)  Removed	(8)  Encapsulated	(9)  Enclosed   	(10) Isolated & Restricted

Miscellaneous:		(11) Inaccessible, no inspection data	    (12) Other (Explain under comments)   	 (13) Non-Asbestos/Not Inspected

CONSULT ORIGINAL AND SUPPLEMENTARY INSPECTION REPORTS FOR MATERIALS WITH TRACE AMOUNTS OF ASBESTOS

SIX MONTH SURVEILLANCE

HOMOGENEOUS ACBM RECORDS	Date of Inspection: __09/28/09______

District: Chico Unified School District	Inspector: Dale Hayes

School: Neal Dow Elementary School                                                                                                                                                                  Building: C																Building: B (FKA C)

| Material Class | Material | Homo. Mat. # | % Asb. | Ft2/L.F. | Location | Condition: Code & Comments | Friable Yes/No |
| --- | --- | --- | --- | --- | --- | --- | --- |
| S | PLASTER TROWELED ON | 2 | 1-5% | 700 S | CENTER OF BUILDING (ALL 3 ROOMS) 918A, K-1, & K-2 | (1) (4) | N |
| M | 9" VFT TAN | 3 | 1-5% | 3,700 S | BACK ROOM (918A) | (1) (4) BACK ROOM - 9" VFT COVERED WITH CARPET, EXCEPT IN COMMON AREA. | N |
| M | TRANSITE PANELS | 99 | ASSUMED | 5,000 F | ABOVE WINDOWS | (12) CANNOT FIND | N |
| M | 12" ACT | 102 | ASSUMED | 3,000 S | ALL 3 ROOMS 918A, K-1, & K-2 | (1) (4) | N |
| M | DRYWALL | 103 | ASSUMED | 1,500 S | THROUGHOUT | (1) | N |

CONDITION CODE

General Condition:	(1) Good	(2)  Damaged	(3)  Significantly Damaged (25% or more)

Change in Condition:	(4) No		(5)  Yes (If Yes, explain under comments)

Abated:		(6) Repaired	(7)  Removed	(8)  Encapsulated	(9)  Enclosed   	(10) Isolated & Restricted

Miscellaneous:		(11) Inaccessible, no inspection data	    (12) Other (Explain under comments)   	 (13) Non-Asbestos/Not Inspected

CONSULT ORIGINAL AND SUPPLEMENTARY INSPECTION REPORTS FOR MATERIALS WITH TRACE AMOUNTS OF ASBESTOS